## BOQ SUMMARY
CHILLER INFORMATION | MAKE | MODEL | CAPACITY [TR] | Area to be Inspected & Considered | SCOPE | REMARK & STATUS
CHILLER 1 | McQuay | ALSF 426.4 4XEST , Serial – 501611/2 | 425 TR | Controls Upgrade | Shall be considered Currently Operational | The system upgrade was not performed; however, the AMC vendor successfully integrated the existing controls with a new EXV driver module, and the unit is now operational. Please note that since these controls are obsolete, the vendor cannot provide further support in the event of a future failure. They strongly recommend a full control system upgrade at the next sign of malfunction.
|  |  |  | EXV DRIVES Upgrade | Not Required | EXV Drives are replaced with new model.
|  |  |  | Condenser Coils Replacement | Need to be considered & replaced | We recommend to replace considering the aging factors
|  |  |  | Cooler body & CHW Pipes Insulation | Need to be considered & replaced | To be considered at the time coil replacement work - considering the aging factors
|  |  |  | Chiller Panels - Full Painting Work | Need to be considered & repainted | To be considered at the time coil replacement work - considering the aging factors
|  |  |  | Valve Packages to inspected on both Primary & Secondary. | Need to be considered & Inspected thoroughly | We recommend to replace based condition report whenever required - considering the aging factors
|  |  |  | All Pumps to inspected (Primary & Secondary) | Need to be considered & Inspected thoroughly | We recommend to replace based condition report whenever required - considering the aging factors
|  |  |  | VFD Control Panels to inspected (Not in Full Operational Currently ) | Need to be considered & Inspected thoroughly | We recommend to thoroughly inspect & make it fully operational for energy efficiency - considering the aging factors
|  |  |  | CHW pipe line circuits are to be inspected & tested | Need to be considered & Inspected thoroughly | We recommend to thoroughly inspect for operational efficiency - considering the aging factors
CHILLER 2 | McQuay | ALSF 426.4 4XEST , Serial – 501611/2 | 425 TR | Controls Upgrade | Supply and Install Microprocessor Controller (UL Listed) Supply and Install Temperature Sensor Supply and Install Current Sensor Supply and Install Pressure Sensor Supply and Install with Voltage Monitor Supply and Install Built-in Ethernet Supply and Install Modbus Supply and Install Bacnet Communication System Supply and Install Sensor Cable Supply and Install Slave Input/output Cables Configuration of Chiller Software Configuration of EXV Driver Card Test and Run the Chiller Benefits of the MCS Magnum retrofit are: It replaces inaccurate sensors and mechanical timers. The system eliminates Nuisance trips through the addition of a PRO-ACTIVE algorithm. The MCS PRO-ACTIVE controller, coupled with the CONTROL ZONE technology, reduces compressor cycling up to 75%, allowing the microprocessor to handle the most unique conditions. The MCS controller will keep the system running at its most optimum level. Dynamic adjustments are made based on low suction PSI, high motor amps, and high discharge PSI, high oil temperature, low ambient, high discharge temperature, etc. Algorithm that provide improved protection against motor overloading, high amp draw, low suction PSI, high discharge PSI, freeze protect, low oil PSI and unsafe suction. A STATE MACHINE that tells you where it is and what it’s doing in simple terms. Single function keypads with a backlit display with exact the data you need. This, coupled with a simple ENGLISH language event log, allows for the easiest to use system available today in the modern industry. An extremely fast WINDOWS based support system provides complete status on all operations both locally and remotely. History, static and dynamic graphic is standard to aid in commissioning, trouble shooting and evaluation. Using the MCS compressor control algorithm and the MCS condenser control algorithm reduces Chiller energy consumption. The installation of this state of the art microprocessor based control retrofit will guaranty accurate and reliable operation, as well as precise monitoring, ensuring that the Chiller operates as efficiently as possible. The upgrade can be partially performed whilst the Chiller remains in operation, ensuring minimum down time for the Chiller. Exclusions & Clarifications: All work to be performed during normal business hours During above mentioned work, if we find any additional work will be quoted separately | Scope as per AMC VENDOR through OEM
|  |  |  | EXV DRIVES Upgrade | Required - Currently nonoperational Spare available | Since the existing EXV drive model is obsolete, the OEM has recommended a new model that requires an upgrade to the system's existing controls. This solution was proposed by the AMC vendor in coordination with the OEM.
|  |  |  | Condenser Coils Replacement | Need to be considered & replaced | We recommend to replace considering the aging factors
|  |  |  | Cooler body & CHW Pipes Insulation | Need to be considered & replaced | To be considered at the time coil replacement work - considering the aging factors
|  |  |  | Chiller Panels - Full Painting Work | Need to be considered & repainted | To be considered at the time coil replacement work - considering the aging factors
|  |  |  | Valve Packages to inspected on both Primary & Secondary. | Need to be considered & Inspected thoroughly | We recommend to replace based condition report whenever required - considering the aging factors
|  |  |  | All Pumps to inspected (Primary & Secondary) | Need to be considered & Inspected thoroughly | We recommend to replace based condition report whenever required - considering the aging factors
|  |  |  | VFD Control Panels to inspected (Not in Full Operational Currently ) | Need to be considered & Inspected thoroughly | We recommend to thoroughly inspect & make it fully operational for energy efficiency - considering the aging factors
|  |  |  | CHW pipe line circuits are to be inspected & tested | Need to be considered & Inspected thoroughly | We recommend to thoroughly inspect for operational efficiency - considering the aging factors
CHILLER 3 | McQuay | ALSF 212.2 ,Serial number – 501609 | 210 TR | Controls Upgrade | Supply and Install Microprocessor Controller (UL Listed) Supply and Install Temperature Sensor Supply and Install Current Sensor Supply and Install Pressure Sensor Supply and Install with Voltage Monitor Supply and Install Built-in Ethernet Supply and Install Modbus Supply and Install Bacnet Communication System Supply and Install Sensor Cable Supply and Install Slave Input/output Cables Configuration of Chiller Software Configuration of EXV Driver Card Test and Run the Chiller Benefits of the MCS Magnum retrofit are: It replaces inaccurate sensors and mechanical timers. The system eliminates Nuisance trips through the addition of a PRO-ACTIVE algorithm. The MCS PRO-ACTIVE controller, coupled with the CONTROL ZONE technology, reduces compressor cycling up to 75%, allowing the microprocessor to handle the most unique conditions. The MCS controller will keep the system running at its most optimum level. Dynamic adjustments are made based on low suction PSI, high motor amps, and high discharge PSI, high oil temperature, low ambient, high discharge temperature, etc. Algorithm that provide improved protection against motor overloading, high amp draw, low suction PSI, high discharge PSI, freeze protect, low oil PSI and unsafe suction. A STATE MACHINE that tells you where it is and what it’s doing in simple terms. Single function keypads with a backlit display with exact the data you need. This, coupled with a simple ENGLISH language event log, allows for the easiest to use system available today in the modern industry. An extremely fast WINDOWS based support system provides complete status on all operations both locally and remotely. History, static and dynamic graphic is standard to aid in commissioning, trouble shooting and evaluation. Using the MCS compressor control algorithm and the MCS condenser control algorithm reduces Chiller energy consumption. The installation of this state of the art microprocessor based control retrofit will guaranty accurate and reliable operation, as well as precise monitoring, ensuring that the Chiller operates as efficiently as possible. The upgrade can be partially performed whilst the Chiller remains in operation, ensuring minimum down time for the Chiller. Exclusions & Clarifications: All work to be performed during normal business hours During above mentioned work, if we find any additional work will be quoted separately | Scope as per AMC VENDOR through OEM
|  |  |  | EXV DRIVES Upgrade | Required - Currently Operational. | Since the existing EXV drive model is obsolete, the OEM has recommended a new model that requires an upgrade to the system's existing controls. This solution was proposed by the AMC vendor in coordination with the OEM.
|  |  |  | Condenser Coils Replacement | Need to be considered & replaced | We recommend to replace considering the aging factors
|  |  |  | Cooler body & CHW Pipes Insulation | Need to be considered & replaced | To be considered at the time coil replacement work - considering the aging factors
|  |  |  | Chiller Panels - Full Painting Work | Need to be considered & repainted | To be considered at the time coil replacement work - considering the aging factors
|  |  |  | Valve Packages to inspected on both Primary & Secondary. | Need to be considered & Inspected thoroughly | We recommend to replace based condition report whenever required - considering the aging factors
|  |  |  | All Pumps to inspected (Primary & Secondary) | Need to be considered & Inspected thoroughly | We recommend to replace based condition report whenever required - considering the aging factors
|  |  |  | VFD Control Panels to inspected (Operational Currently ) | Need to be considered & Inspected thoroughly | We recommend to thoroughly inspect & make it fully operational for energy efficiency - considering the aging factors
|  |  |  | CHW pipe line circuits are to be inspected & tested | Need to be considered & Inspected thoroughly | We recommend to thoroughly inspect for operational efficiency - considering the aging factors
CHILLER 4 | McQuay | ALSF 358.3 ,Serial – 501610/2 | 350 TR | Controls Upgrade | Shall be considered Currently Operational | Upgradation was not done, However AMC vendor has supported to intergrade the existing controls with New EXV driver modal - Now in working condition. Though the Controls are obsolete in market, they will not able further support in case any failure, they even recommend to upgrade the controls whenever the systems fails.
|  |  |  | EXV DRIVES Upgrade | Required - Currently Operational. | Since the existing EXV drive model is obsolete, the OEM has recommended a new model that requires an upgrade to the system's existing controls. This solution was proposed by the AMC vendor in coordination with the OEM.
|  |  |  | Condenser Coils Replacement | Completed Apr'23 _ Not Required
|  |  |  | Cooler body & CHW Pipes Insulation | Need to be considered & replaced | To be considered at the time coil replacement work - considering the aging factors
|  |  |  | Chiller Panels - Full Painting Work | Completed Apr'23 _ Not Required
|  |  |  | Valve Packages to be inspected on both Primary & Secondary. | Need to be considered & Inspected thoroughly | We recommend to replace based condition report whenever required - considering the aging factors
|  |  |  | All Pumps to be inspected (Primary & Secondary) | Need to be considered & Inspected thoroughly | We recommend to replace based condition report whenever required - considering the aging factors
|  |  |  | VFD Control Panels to inspected (Operational Currently ) | Need to be considered & Inspected thoroughly | We recommend to thoroughly inspect & make it fully operational for energy efficiency - considering the aging factors
|  |  |  | CHW pipe line circuits are to be inspected & tested | Need to be considered & Inspected thoroughly | We recommend to thoroughly inspect for operational efficiency - considering the aging factors
CHILLER 5 | McQuay | ALSF 358.3 ,Serial – 501610/2 | 350 TR | Controls Upgrade | Shall be considered Currently Operational | Upgradation was not done, However AMC vendor has supported to intergrade the existing controls with New EXV driver modal - Now in working condition. Though the Controls are obsolete in market, they will not able further support in case any failure, they even recommend to upgrade the controls whenever the systems fails.
|  |  |  | EXV DRIVES Upgrade | Not Required | EXV Drives are replaced with new model.
|  |  |  | Condenser Coils Replacement | Completed Apr'23 _ Not Required
|  |  |  | Cooler body & CHW Pipes Insulation | Need to be considered & replaced | To be considered at the time coil replacement work - considering the aging factors
|  |  |  | Chiller Panels - Full Painting Work | Completed Apr'23 _ Not Required
|  |  |  | Valve Packages to be inspected on both Primary & Secondary. | Need to be considered & Inspected thoroughly | We recommend to replace based condition report whenever required - considering the aging factors
|  |  |  | All Pumps to be inspected (Primary & Secondary) | Need to be considered & Inspected thoroughly | We recommend to replace based condition report whenever required - considering the aging factors
|  |  |  | VFD Control Panels to inspected (Operational Currently ) | Need to be considered & Inspected thoroughly | We recommend to thoroughly inspect & make it fully operational for energy efficiency - considering the aging factors
|  |  |  | CHW pipe line circuits are to be inspected & tested | Need to be considered & Inspected thoroughly | We recommend to thoroughly inspect for operational efficiency - considering the aging factors

## Techinical SPEC
CHILLER INFORMATION | CHILLER 1 |  |  | CHILLER 2 |  |  | CHILLER 3 |  |  | CHILLER 4 |  |  | CHILLER 5
MAKE | McQuay |  |  | McQuay |  |  | McQuay |  |  | McQuay |  |  | McQuay
MODEL | ALS E 426.4 XE ST |  |  | ALS E 426.4 XE ST |  |  | ALS E 212.2 XE ST |  |  | ALS E 358.3 XE ST |  |  | ALS E 358.3 XE ST
REFRIGERANT | 134a |  |  | 134a |  |  | 134a |  |  | 134a |  |  | 134a
CHILLER OPERATION MODE - RUN/STAND BY | RUN |  |  | RUN |  |  | RUN |  |  | RUN |  |  | RUN
CHILLER RUNNING HOURS PER DAY | 24 Hours |  |  | 24 Hours |  |  | 24 Hours |  |  | 24 Hours |  |  | 24 Hours
CAPACITY [RT] | 425 TR |  |  | 425 TR |  |  | 210 TR |  |  | 350 TR |  |  | 350 TR
CHILLER MOTOR RATING - HP/KW
COMPRESSOR FLA (%) (Total FLA) | 1269.2 |  |  | 1269.2 |  |  | 634.6 |  |  | 1052.4 |  |  | 1052.4
COMPRESSOR RUNNING (KW)
VOLTS (R/Y/B) | 400 /460 | 400 /460 | 400 /460 | 400 /460 | 400 /460 | 400 /460 | 400 /460 | 400 /460 | 400 /460 | 400 /460 | 400 /460 | 400 /460 | 400 /460 | 400 /460 | 400 /460
AMPERES (R/Y/B) | 201 | 204 | 204 | 202 | 203 | 203 | 203 | 204 | 204 | 202 | 205 | 205 | 201 | 203 | 203
POWER FACTOR (pf) | 0.94/0.98 |  |  | 0.94/0.98 |  |  | 0.94/0.98 |  |  | 0.94/0.98 |  |  | 0.94/0.98
FREQUENCY (Hz) | 50/60 Hz |  |  | 50/60 Hz |  |  | 50/60 Hz |  |  | 50/60 Hz |  |  | 50/60 Hz
CHWST [°F/°C] | 8°C |  |  | 8°C |  |  | 8°C |  |  | 7°C |  |  | 7°C
CHWRT [°F/°C] | 10°C |  |  | 10°C |  |  | 10°C |  |  | 9°C |  |  | 9°C
CWST [°F/°C] FOR WATER COOLED SYSTEM | Not Applicable |  |  | Not Applicable |  |  | Not Applicable |  |  | Not Applicable |  |  | Not Applicable
CWRT [°F/°C] FOR WATER COOLED SYSTEM | Not Applicable |  |  | Not Applicable |  |  | Not Applicable |  |  | Not Applicable |  |  | Not Applicable
REFRIGERANT SUCTION PRESSURE - PSIG | 2.2 Bar |  |  | 2.2 Bar |  |  | 2.2 Bar |  |  | 2.1 |  |  | 2.1
REFRIGERANT CONDENSING PRESSURE - PSIG | 15.5 Bar |  |  | 15.5 Bar |  |  | 15.5 Bar |  |  | 15.3 |  |  | 15.3
SATURATED EVAPORATOR TEMPERATURE | 7.3°C |  |  | 7.3°C |  |  | 7.3°C |  |  | 7.2°C |  |  | 7.2°C
SATURATED CONDENSING TEMPERATURE | 53°C |  |  | 53°C |  |  | 53°C |  |  | 53°C |  |  | 53°C
EVAPORATOR PRESSURE DROP, PSIG/FEET
MAKE UP WATER CONSUMPTION/DAY - KL/DAY or GALLONS/DAY | 2 gal/day |  |  | 2 gal/day |  |  | 2 gal/day |  |  | 2 gal/day |  |  | 2 gal/day
CONDENSER FLOWRATE (m³hr / gpm) | Not Applicable |  |  | Not Applicable |  |  | Not Applicable |  |  | Not Applicable |  |  | Not Applicable
EVAPORATOR FLOWRATE (m³hr / gpm) | 9.9 |  |  | 9.9 |  |  | 9.9 |  |  | 9.9 |  |  | 9.9
TOTAL (KWh)
CHILLER INTERFACE - YES /NO | NO |  |  | NO |  |  | NO |  |  | NO |  |  | NO
CONDENSER TYPE - AIR COOLED/EVAPORATIVE OR WATER COOLED | Air Cooled |  |  | Air Cooled |  |  | Air Cooled |  |  | Air Cooled
VFD KW AND % OF SPEED | NO |  |  | NO |  |  | NO |  |  | NO |  |  | NO
AVAILABILITY OF BMS | NO |  |  | NO |  |  | NO |  |  | NO |  |  | NO
CHILLED WATER PRIMARY PUMP INFORMATION | PUMP 1 |  | PUMP 2 |  | PUMP 3 |  | PUMP 4 |  | PUMP 1 |  | PUMP 2 |  | PUMP 3
| CHILLER # 1,2 and 3 | [7 empty] | CHILLER # 4 and 5
MAKE | VEMAT |  | MOTOGEN ITALIA |  | MOTOGEN ITALIA |  | MOTOGEN ITALIA |  | VEMAT |  | VEMAT |  | VEMAT
PUMP TYPE | VTB 160L |  | 160L48 |  | 160L48 |  | 160L48 |  | VTB 160L |  | VTB 160L |  | VTB 160L
POWER (KW) | 15KW |  | 15KW |  | 15KW |  | 15KW |  | 15KW |  | 15KW |  | 15KW
VOLT (R/Y/B) | 380V |  | 400V |  | 400V |  | 400V |  | 380V |  | 380V |  | 380V
AMPERE (R/Y/B) | 29.1A |  | 30A |  | 30A |  | 30A |  | 29.1A |  | 29.1A |  | 29.1A
POWER FACTOR (pf) | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8 |  | 0.8
CAPACITY [m³hr / gpm]
DISCHARGE PRESSURE (kg/psi) | Not available |  | Not available |  | Not available |  | Not available |  | Not available |  | Not available |  | Not available
SUCTION PRESSURE (kg/psi) | Not available |  | Not available |  | Not available |  | Not available |  | Not available |  | Not available |  | Not available
PUMP HEAD - MIN/MAX | Not available |  | Not available |  | Not available |  | Not available |  | Not available |  | Not available |  | Not available
VFD KW AND % OF SPEED | Not Applicable |  | Not Applicable |  | Not Applicable |  | Not Applicable |  | Not Applicable |  | Not Applicable |  | Not Applicable
CHILLED WATER SECONDARY PUMP INFORMATION | PUMP 1 |  | PUMP 2 |  | PUMP 3 |  | PUMP 4 |  | PUMP 1 |  | PUMP 2 |  | PUMP 3
| CHILLER # 1,2 and 3 | [7 empty] | CHILLER # 4 and 5
MAKE | FFD AUSTRIA |  | FFD AUSTRIA |  | FFD AUSTRIA |  | FFD AUSTRIA |  | FFD AUSTRIA |  | FFD AUSTRIA |  | FFD AUSTRIA
PUMP TYPE | DPIG 2001 |  | DPIG 2001 |  | DPIG 2001 |  | DPIG 2001 |  | DPIG 2001 |  | DPIG 2001 |  | DPIG 2001
POWER (KW) | 30 |  | 30 |  | 30 |  | 30 |  | 30 |  | 30 |  | 30
VOLT (R/Y/B) | 380 |  | 380 |  | 380 |  | 380 |  | 380 |  | 380 |  | 380
AMPERE (R/Y/B) | 58A |  | 58A |  | 58A |  | 58A |  | 58A |  | 58A |  | 58A
POWER FACTOR (pf) | 0.86 |  | 0.86 |  | 0.86 |  | 0.86 |  | 0.86 |  | 0.86 |  | 0.86
CAPACITY [m³hr / gpm]
CHILLER WITH AIR COOLED/EVAPORATIVE CONDENSER INFORMATION | CHILLER 1 |  | CHILLER 2 |  | CHILLER 3 |  | CHILLER 4 |  | CHILLER 5
MAKE | McQuay |  | McQuay |  | McQuay |  | McQuay |  | McQuay
MODEL | ASL E426.4 XE ST |  | ASL E426.4 XE ST |  | ASL E212.2 XE ST |  | ASL E358.3 XE ST |  | ASL E358.3 XE ST
REFRIGERANT | 134a |  | 134a |  | 134a |  | 134a |  | 134a
CHWST [°F/°C] - EVAPORATOR | 8°C |  | 8°C |  | 8°C |  | 7°C |  | 7°C
CHWRT [°F/°C] - EVAPORATOR | 10°C |  | 10°C |  | 10°C |  | 9°C |  | 9°C
CHILLED WATER FLOW
CONDENSER AIR ENTERING TEMPERATURE | Ambient air temperature |  | Ambient air temperature |  | Ambient air temperature |  | Ambient air temperature |  | Ambient air temperature
NO OF COMPRESSORS PER CHILLER | 4 |  | 4 |  | 2 |  | 3 |  | 3
NO OF FANS PER CIRCUIT | 26 Per Chiller |  | 26 Per Chiller |  | 13 Per Chiller |  | 22 Per Chiller |  | 22 Per Chiller
POWER COMPRESSOR (KW)
POWER FAN (KW)
AMBIENT TEMPERATURE
HUMIDITY - Rh
COOLER WATER PRESSURE - ΔP
COOLING CAPACITY